## Schedule of loads
Circuit No. | Load Description | No. of Outlets |  | Switches |  |  |  | Load Rating |  |  |  | CB rating |  |  | Number, Size and Type of Wire | Conduit
|  | CO/SAO/ACU | LO | S1 | S2 | S3 | S3W | HP | Volts | Volt Ampere | Ampere | Phase | AT | AF
1 | Lighting Outlet |  | 32 | - | 8 | - | - | - | 230 | 760 | 3.3043 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
2 | Lighting Outlet |  | 40 | 4 | 3 | - | - | - | 230 | 800 | 3.4783 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
3 | Convenience Outlet 1 | 10 |  | - | - | - | - | - | 230 | 1800 | 7.8261 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
4 | Convenience Outlet 2 | 10 |  | - | - | - | - | - | 230 | 1800 | 7.8261 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
5 | Convenience Outlet 3 | 5 |  | - | - | - | - | - | 230 | 900 | 3.913 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
6 | Convenience Outlet 4 | 10 |  | - | - | - | - | - | 230 | 1800 | 7.8261 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
7 | Bathroom Outlet | 8 |  | - | - | - | - | - | 230 | 1440 | 6.2609 | 1 | 15 | 100 | 2-2.0mm2 THHW | 16mmф PVC Sched 40
8 | Water Heater 01 | 1 |  | - | - | - | - | - | 230 | 3000 | 13.0435 | 1 | 20 | 100 | 2-3.5mm2 THHW | 16mmф PVC Sched 40
9 | Water Heater 02 | 1 |  | - | - | - | - | - | 230 | 3000 | 13.0435 | 1 | 20 | 100 | 2-3.5mm2 THHW | 16mmф PVC Sched 40
10 | Water Heater 03 | 1 |  | - | - | - | - | - | 230 | 3000 | 13.0435 | 1 | 20 | 100 | 2-3.5mm2 THHW | 16mmф PVC Sched 40
11 | Water Heater 04 | 1 |  | - | - | - | - | - | 230 | 3000 | 13.0435 | 1 | 20 | 100 | 2-3.5mm2 THHW | 16mmф PVC Sched 40
12 | Garage Outlet | 4 |  | - | - | - | - | - | 230 | 720 | 3.1304 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
13 | Laundry Outlet | 4 |  | - | - | - | - | - | 230 | 1500 | 6.5217 | 1 | 15 | 100 | 2-2.0mm2 THHW | 16mmф PVC Sched 40
14 | Small Appliance Circuit 01 | 6 |  | - | - | - | - | - | 230 | 1500 | 6.5217 | 1 | 15 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
15 | Airconditioning Unit 01 | 1 |  | - | - | - | - | 2 | 230 | 2760 | 12 | 1 | 25 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
16 | Airconditioning Unit 02 | 1 |  | - | - | - | - | 1.5 | 230 | 2300 | 10 | 1 | 20 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
17 | Airconditioning Unit 03 | 1 |  | - | - | - | - | 1.5 | 230 | 2300 | 10 | 1 | 20 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
18 | Airconditioning Unit 04 | 1 |  | - | - | - | - | 1.5 | 230 | 2300 | 10 | 1 | 20 | 100 | 2-2.0mm2 THHN | 16mmф PVC Sched 40
19 | Water Pump | 1 |  | - | - | - | - | 2 | 230 | 2760 | 12 | 1 | 15 | 100 | 2-2.0mm2 THHW | 16mmф PVC Sched 40
| Transformer | [7 empty] | 230 | 37500 | 163.0435 | 1 | 175 | 100 | 2-50.0mm2 THHN
| Generator | [7 empty] | 230 | 50000 | 217.3913 | 1 | 225 | 100 | 2-50.0mm2 THHN

## Load calculation
General Lighting and Convenience Receptacle |  |  | Application of Demand Factor |  |  | Service Entrance Conductors
Lighting outlet | 1560 | VA | First 3,000VA at 100% DF | 3000 | VA | I = | 1.25(2760) | + 28167 | = | 137.4652 | A
Convenience Outlet 01 | 1800 | VA | Remainder at 35% DF | 3507 | VA |  | 230 |  |  |  | ✔ | Use 2-50.0mm2 THHN Cu Wire in 35mm ᴓ RMC
Convenience Outlet 02 | 1800 | VA | [9 empty] | Use 2-22mm2 THHN Cu Wire in Free Air
Convenience Outlet 03 | 900 | VA | Other Load: | [8 empty] | Use 1-22mm2 THHN Cu Wire as Grounding Conductor
Convenience Outlet 04 | 1800 | VA | 4- 3kW Water Heater | 12000 | VA | Service Equipment
Bathroom outlet | 1440 | VA | 1- 2HP ACU | 2760 | VA
Garage Outlet | 720 | VA | 3- 1.5HP ACU | 6900 | VA | I = | 2.5(2760) | + 28167 | = | 152.4652 | A | Use 1-175 AT MCB
|  |  | 1- 2HPWaterpump | 2760 | VA |  | 230
Laundry Circuit
|  |  | Total Net Computed Load | 30927 | VA
Laundry Outlet | 1500 | VA |  |  |  | Transformer Requirement
Small Appliance Load | [5 empty] | Total Net Computed Load |  |  | = | 30927
Small Appliance Outlet | 1500 | VA |  |  |  | Use 1-37.5kVA 7.62/0.23kV, %Z=1.7 60Hz 1ᴓ, Pole Mounted Distribution Transformer
Sub-Total | 13020 | VA |  |  |  | Generator Requirement
[6 empty] | Total Net Computed Load |  |  | = | 30927
[6 empty] | Generator Size |  | 1.25X | = | 38658.75
Use 1-50kVA 230V 60Hz 1ᴓ, Standby Generator

## Voltage Drop
Voltage Drop Calculation
Voltage Drop feeder |  |  |  | Voltage Drop Farthest Outlet |  |  |  | Total Voltage Drop
Service Conductor Length |  | 11 | meters | Service Conductor Length |  | 24 | meters | VD | VD1+VD2
Conductor Rfeeder |  | 0.127 | ohm/kft | Conductor Rbranch |  | 3.19 | ohm/kft | VD | 4.5352
Total Load |  | 137.4652 | A | Total Load |  | 6.5217 | A | %VD2 | 1.972%
[8 empty] | Remarks | PASSED
VD1 | 1.2598 |  |  | VD2 | 3.2754
%D1 | 0.5477% |  |  | %D2 | 1.424%
Remarks | PASSED |  |  | Remarks | PASSED
V1 | 228.7402 |  |  | V2 | 225.4648

## Short Circuit
Short Circuit Calculation
Use 1-37.5kVA 7.62/0.23kV, %Z=1.7 60Hz 1ᴓ, Pole Mounted Distribution Transformer |  |  |  |  | Short Circuit Current @ Panel Board
KVA= | 37.5 |  |  |  | L | = | 11
%Z= | 1.7% |  |  |  | ICS | = | 9590.7928
[5 empty] | V | = | 230
[5 empty] | C | = | 8925
IFL | KVA X 1000 | = | 163.0435 | A | n | = | 1
230
[5 empty] | f | = | L X ISC | 0.16857
Multiplier | 100 | = | 58.8235 |  |  |  | V X C n
1.7%
[5 empty] | Multiplier | = | 1 | 0.85575
1 + f
Short Circuit Current @ Secondary Transformer
[5 empty] | ISC2 | = | Multi X ISC1 | 8207.2772 | A
ISC1 | Multi X IFL | = | 9590.7928 | A