## IEEE
Relay 1 | [5 empty] | Relay 2 | [6 empty] | Time | Fault
Relay Rating = | 5 | Amp |  |  |  | Relay Rating = | 5 | Amp |  |  |  | 1 | 0.01 | 1000
Pick Up Current= | 100 | Amp |  |  |  | Pick Up Current= | 70 | Amp |  |  |  | 2 | 100 | 1000
CTR = | 200 |  |  |  |  | CTR = | 100
TD = | 0.99428 |  |  |  |  | TD = | 0.4 |  |  |  |  | Time1 | 0.40422 | sec
[12 empty] | Time2 | 0.10422 | sec
Curve Name |  |  | A | B | P | Curve Name |  |  | A | B | P |  | 0.3 | sec
IEEE Extremely Inverse |  | IEEE | 28.2 | 0.1217 | 2 | IEEE Extremely Inverse |  | IEEE | 28.2 | 0.1217 | 2
IEEE Very Inverse | IEEE Very Inverse | IEEE | 19.61 | 0.491 | 2 | IEEE Very Inverse | IEEE Very Inverse | IEEE | 19.61 | 0.491 | 2
IEEE Inverse | IEEE Inverse | IEEE | 0.0515 | 0.114 | 0.02 | IEEE Inverse | IEEE Inverse | IEEE | 0.0515 | 0.114 | 0.02
M | Current | EI | VI | I |  | M | Current | EI | VI | I
1.5 | 150 | 22.552 | 16.0865 | 6.4022 |  | 1.5 | 105 | 9.0727 | 6.4716 | 2.5756
2 | 200 | 9.4673 | 6.9875 | 3.7815 |  | 2 | 140 | 3.8087 | 2.8111 | 1.5213
3 | 300 | 3.6259 | 2.9254 | 2.4183 |  | 3 | 210 | 1.4587 | 1.1769 | 0.97288
4 | 400 | 1.9903 | 1.7881 | 1.9347 |  | 4 | 280 | 0.80068 | 0.71933 | 0.77834
5 | 500 | 1.2893 | 1.3006 | 1.6787 |  | 5 | 350 | 0.51868 | 0.52323 | 0.67533
6 | 600 | 0.92211 | 1.0453 | 1.5168 |  | 6 | 420 | 0.37097 | 0.42051 | 0.61022
7 | 700 | 0.70515 | 0.8944 | 1.4036 |  | 7 | 490 | 0.28368 | 0.35982 | 0.56468
8 | 800 | 0.56606 | 0.79768 | 1.3192 |  | 8 | 560 | 0.22773 | 0.32091 | 0.5307
9 | 900 | 0.47149 | 0.73192 | 1.2532 |  | 9 | 630 | 0.18968 | 0.29445 | 0.50415
10 | 1000 | 0.40422 | 0.68514 | 1.1999 |  | 10 | 700 | 0.16262 | 0.27563 | 0.4827
11 | 1100 | 0.35466 | 0.65068 | 1.1557 |  | 11 | 770 | 0.14268 | 0.26177 | 0.46493
12 | 1200 | 0.31708 | 0.62454 | 1.1183 |  | 12 | 840 | 0.12756 | 0.25125 | 0.44989
13 | 1300 | 0.2879 | 0.60425 | 1.0861 |  | 13 | 910 | 0.11582 | 0.24309 | 0.43696
14 | 1400 | 0.26479 | 0.58818 | 1.0581 |  | 14 | 980 | 0.10653 | 0.23663 | 0.42568
15 | 1500 | 0.24618 | 0.57524 | 1.0334 |  | 15 | 1050 | 0.099037 | 0.23142 | 0.41574
16 | 1600 | 0.23096 | 0.56466 | 1.0114 |  | 16 | 1120 | 0.092915 | 0.22716 | 0.40689
17 | 1700 | 0.21836 | 0.55589 | 0.99165 |  | 17 | 1190 | 0.087847 | 0.22364 | 0.39894
18 | 1800 | 0.20781 | 0.54856 | 0.97379 |  | 18 | 1260 | 0.083603 | 0.22068 | 0.39175
19 | 1900 | 0.19889 | 0.54235 | 0.95753 |  | 19 | 1330 | 0.080013 | 0.21819 | 0.38521
20 | 2000 | 0.19128 | 0.53706 | 0.94264 |  | 20 | 1400 | 0.076951 | 0.21606 | 0.37923
21 | 2100 | 0.18473 | 0.53251 | 0.92895 |  | 21 | 1470 | 0.074316 | 0.21423 | 0.37372
22 | 2200 | 0.17906 | 0.52856 | 0.9163 |  | 22 | 1540 | 0.072034 | 0.21264 | 0.36863
23 | 2300 | 0.17411 | 0.52512 | 0.90456 |  | 23 | 1610 | 0.070044 | 0.21126 | 0.3639
24 | 2400 | 0.16977 | 0.5221 | 0.89363 |  | 24 | 1680 | 0.068297 | 0.21004 | 0.35951
25 | 2500 | 0.16594 | 0.51944 | 0.88342 |  | 25 | 1750 | 0.066757 | 0.20897 | 0.3554
26 | 2600 | 0.16254 | 0.51708 | 0.87384 |  | 26 | 1820 | 0.065391 | 0.20802 | 0.35155
27 | 2700 | 0.15952 | 0.51498 | 0.86485 |  | 27 | 1890 | 0.064175 | 0.20717 | 0.34793
28 | 2800 | 0.15681 | 0.51309 | 0.85637 |  | 28 | 1960 | 0.063086 | 0.20642 | 0.34452
29 | 2900 | 0.15438 | 0.5114 | 0.84837 |  | 29 | 2030 | 0.062109 | 0.20574 | 0.3413
30 | 3000 | 0.15219 | 0.50988 | 0.84079 |  | 30 | 2100 | 0.061227 | 0.20513 | 0.33825
10 | 1000 | 0.40422 |  |  |  | 14.2857 | 1000 | 0.10422
200:5
100:5
620 A